## Sheet1
Tag | iGreen database tag name | Description | Units | Questions
FIT_900_002_P.PV | Final Product Flow (FIT-900-002) | Product water Delivery Flow | gpm
PIT_900_003_P.PV | Final Product Pressure (PIT-900-003) | Product delivery pressure | psi
Added by Frits for calc Power | P-900-001/1 Actual Speed
Added by Frits for calc Power | P-900-001/2 Actual Speed
AIT_900_003_P.PV | Final Product Conductivity (AIT-900-003) | Conductivity Product Tank Discharge | uS/cm
AIT_900_006_P.PV | Lime Water Conductivity (AIT-900-006) | Conductivity Lime water Buffer Tank | uS/cm
RO_UCL.TDS_SW | Not in database, to be calculated from Intake Conductivity (AIT-100-001) | TDS Seawater (calculated) | ppt
PIT_100_001_P.PV | Intake Discharge Pressure (PIT-100-001) | Seawater inlet pressure | psi
PT_100_002_P.PV | Intake Discharge Pressure (PIT-100-002) | Seawater effluent pressure | psi
TIT_100_002_P.PV | Intake Temperature (TIT-100-002) | Seawater inlet temperature | F
AIT_100_001_P.PV | Intake Conductivity (AIT-100-001) | Conductivity Seawater | uS/cm
AIT_100_002_P.PV | Intake pH (AIT-100-002) | pH Seawater | -
AIT_100_003_P.PV | Final Product Conductivity (AIT-900-003) | Turbidity Seawater | -
FIT_100_001_P.PV | Intake Flow (FIT-100-001) | Intake Flow | gpm
P_100_001_1_P.HOURS | P100-001/1 HoursLast without Interval | Intake Pump 1 | min
P_100_001_2_P.HOURS | P100-001/2 HoursLast without Interval | Intake Pump 2 | min
MPDA_kW | MPDA_kW | MPD A power Consumption | kW
| Not in Database, to be calcuated from the pump curve | Power of the HP pump - from VFD in MPD A | kW
| Not in Database, to be calcuated from the pump curve | Power of the circ pump - from VFD in MPD A | kW
| Not in Database, to be calcuated from the pump curve | Power of the circ pump - from VFD in MPD A | kW
AIT_400_001A_P.PV | Train A Product Conductivity (AIT-400-001A) | Conductivity Product MPD | uS/cm
FIT_200_001A_P.PV | PT Feed Flow (FIT-200-001A) | Seawater Inlet Flow MPD | Process Value in GPM
FIT_200_002A_P.PV | BW Pump P-200-002A Discharge Flow (FIT-200-002A) | PT Backwash Flow MPD | Process Value in GPM
FIT_200_004A_P.PV | BW Tank T-200-003A Feed Flow (FIT-200-004A) | BW Tank Filling Flow | Process Value in GPM
FIT_400_001A_P.PV | Train A Brine Flow (FIT-400-001A) | Low Pressure Brine Flow MPD | Process Value in GPM
FIT_400_002A_P.PV | Train A Product Flow (FIT-400-002A) | Product Flow MPD | Process Value in GPM
LT_200_002A_P.PV | BW Tank T-200-003A Level (LIT-200-002A) | Level Backwash Tank MPD | Level in Feet
P_200_001A_P.RPM_MV | RO Feed Pump P-200-001A Actual Speed | RO Feed Pump- MPD A | Speed reference
P_200_002A_P.RPM_MV | BW Pump P-200-002A Actual Speed | BW Pump- MPD A | Speed reference
P_400_001A_P.RPM_MV | P-400-001A Actual Speed | ERS Circulation Pump - MPD A | Speed reference
P_400_002A_P.RPM_MV | P-400-002A Actual Speed | HP Pump - MPD A | Speed reference | Pump speed MPD A
PDIT_200_001A_P.PV | Micronic Filters Diff. Pressure (PDIT-200-001A) | Differential Pressure MF - MPD A | Process Value in PSI
PDIT_400_001A_P.PV | Train A Feed-Brine Diff. Pressure (PDIT-400-001A) | Differential Pressure RO Train - MPD A | Process Value in PSI | Pressure drop across all pressure vessels in A
PDIT_400_002A_P.PV | P-400-002A Diff. Pressure (PDIT-400-002A) | Differential Pressure ERS Cir. Pump - MPD A | Process Value in PSI | Pressure increase across circ pump
PIT_400_003A_P.PV | P-400-002A Discharge Pressure (PIT-400-003A) | Feed Pressure RO Train - MPD A | Process Value in PSI | Applied pressure of the RO feed
PT_200_005A_P.PV | Blower Discharge Pressure (PT-200-005A) | Pressure air discharge Blower MPD - MPD A | Process Value in PSI
PT_200_006A_P.PV | RO Feed Pump P-200-001A Suction Pressure (PT-200-006A) | Suction Pressure RO Feed Pump MPD - MPD A | Process Value in PSI
PT_200A_Tags.Q_Filtrate_PV | RO Feed Pump P-200-001A Discharge Flow (Calc.) | Total Filtration Flow - MPD A | Process Value in GPM | Is this post media filter or cartridge filter?
PT_200A_Tags.Q_RO_Feed_PV | Train A Feed Flow (Calc.) | Flow to RO Unit | Process Value in GPM
PT_400_002A_P.PV | P-400-002A Suction Pressure (PT-400-002A) | Suction Pressure HP Pump MPD - MPD A | Process Value in PSI
Q_400_001A_P.PV | P-400-002A Flow (Calc.) | HP discharge flow ERS Cir Pump - MPD A | Process Value in GPM
Q_400_002A | Train A Feed Flow (Calc.) | Feed Flow RO Train - MPD A | Process Value in GPM
RO_300A_Tags.RO.Recovery | Train A Recovery PV | Recovery RO Train - MPD A | Process Value in %
MPDB_kW | MPDB_kW | MPD power Consumption | kW
| Not in Database, to be calcuated from the pump curve | Power of the HP pump - from VFD in MPD A | kW
| Not in Database, to be calcuated from the pump curve | Power of the circ pump - from VFD in MPD A | kW
| Not in Database, to be calcuated from the pump curve | Power of the circ pump - from VFD in MPD A | kW
AIT_400_001B_P.PV | Train B Product Conductivity (AIT-400-001B) | Conductivity Product MPD | uS/cm
FIT_200_001B_P.PV | PT Feed Flow (FIT-200-001B) | Seawater Inlet Flow MPD | Process Value in GPM
FIT_200_002B_P.PV | BW Pump P-200-002B Discharge Flow (FIT-200-002B) | PT Backwash Flow MPD | Process Value in GPM
FIT_200_004B_P.PV | BW Tank T-200-003B Feed Flow (FIT-200-004B) | BW Tank Filling Flow | Process Value in GPM
FIT_400_001B_P.PV | Train B Brine Flow (FIT-400-001B) | Low Pressure Brine Flow MPD | Process Value in GPM
FIT_400_002B_P.PV | Train B Product Flow (FIT-400-002B) | Product Flow MPD | Process Value in GPM
LT_200_002B_P.PV | BW Tank T-200-003B Level (LIT-200-002B) | Level Backwash Tank MPD | Level in Feet
P_200_001B_P.RPM_MV | RO Feed Pump P-200-001B Actual Speed | RO Feed Pump- MPD | Speed reference
P_200_002B_P.RPM_MV | BW Pump P-200-002B Actual Speed | BW Pump- MPD | Speed reference
P_400_001B_P.RPM_MV | P-400-001B Actual Speed | ERS Circulation Pump - MPD | Speed reference
P_400_002B_P.RPM_MV | P-400-002B Actual Speed | HP Pump - MPD | Speed reference
PDIT_200_001B_P.PV | Micronic Filters Diff. Pressure (PDIT-200-001B) | Differential Pressure MF - MPD | Process Value in PSI
PDIT_400_001B_P.PV | Train B Feed-Brine Diff. Pressure (PDIT-400-001B) | Differential Pressure RO Train - MPD | Process Value in PSI | Pressure drop across all pressure vessels in A
PDIT_400_002B_P.PV | P-400-002B Diff. Pressure (PDIT-400-002B) | Differential Pressure ERS Cir. Pump - MPD | Process Value in PSI | Pressure increase across circ pump
PIT_400_003B_P.PV | P-400-002B Discharge Pressure (PIT-400-003B) | Feed Pressure RO Train - MPD | Process Value in PSI | Applied pressure of the RO feed
PT_200_005B_P.PV | Blower Discharge Pressure (PT-200-005B) | Pressure air discharge Blower MPD | Process Value in PSI
PT_200_006B_P.PV | RO Feed Pump P-200-001B Suction Pressure (PT-200-006B) | Suction Pressure RO Feed Pump MPD | Process Value in PSI
PT_200B_Tags.Q_Filtrate_PV | RO Feed Pump P-200-001B Discharge Flow (Calc.) | Total Filtration Flow | Process Value in GPM | Is this post media filter or cartridge filter?
PT_200B_Tags.Q_RO_Feed_PV | Train B Feed Flow (Calc.) | Flow to RO Unit | Process Value in GPM
PT_400_002B_P.PV | P-400-002B Suction Pressure (PT-400-002B) | Suction Pressure HP Pump MPD | Process Value in PSI
Q_400_001B_P.PV | P-400-002B Flow (Calc.) | HP discharge flow ERS Cir Pump | Process Value in GPM
Q_400_002B | Train B Feed Flow (Calc.) | Feed Flow RO Train | Process Value in GPM
RO_300B_Tags.RO.Recovery | Train B Recovery PV | Recovery RO Train | Process Value in %
MPDC_kW | MPDC_kW | MPD power Consumption | kW
| Not in Database, to be calcuated from the pump curve | Power of the HP pump - from VFD in MPD A | kW
| Not in Database, to be calcuated from the pump curve | Power of the circ pump - from VFD in MPD A | kW
| Not in Database, to be calcuated from the pump curve | Power of the circ pump - from VFD in MPD A | kW
AIT_400_001C_P.PV | Train C Product Conductivity (AIT-400-001C) | Conductivity Product MPD | uS/cm
FIT_200_001C_P.PV | PT Feed Flow (FIT-200-001C) | Seawater Inlet Flow MPD | Process Value in GPM
FIT_200_002C_P.PV | BW Pump P-200-002C Discharge Flow (FIT-200-002C) | PT Backwash Flow MPD | Process Value in GPM
FIT_200_004C_P.PV | BW Tank T-200-003C Feed Flow (FIT-200-004C) | BW Tank Filling Flow | Process Value in GPM
FIT_400_001C_P.PV | Train C Brine Flow (FIT-400-001C) | Low Pressure Brine Flow MPD | Process Value in GPM
FIT_400_002C_P.PV | Train C Product Flow (FIT-400-002C) | Product Flow MPD | Process Value in GPM
LT_200_002C_P.PV | BW Tank T-200-003C Level (LIT-200-002C) | Level Backwash Tank MPD | Level in Feet
P_200_001C_P.RPM_MV | RO Feed Pump P-200-001C Actual Speed | RO Feed Pump- MPD | Speed reference
P_200_002C_P.RPM_MV | BW Pump P-200-002C Actual Speed | BW Pump- MPD | Speed reference
P_400_001C_P.RPM_MV | P-400-001C Actual Speed | ERS Circulation Pump - MPD | Speed reference
P_400_002C_P.RPM_MV | P-400-002C Actual Speed | HP Pump - MPD | Speed reference
PDIT_200_001C_P.PV | Micronic Filters Diff. Pressure (PDIT-200-001C) | Differential Pressure MF - MPD | Process Value in PSI
PDIT_400_001C_P.PV | Train C Feed-Brine Diff. Pressure (PDIT-400-001C) | Differential Pressure RO Train - MPD | Process Value in PSI | Pressure drop across all pressure vessels in A
PDIT_400_002C_P.PV | P-400-002C Diff. Pressure (PDIT-400-002C) | Differential Pressure ERS Cir. Pump - MPD | Process Value in PSI | Pressure increase across circ pump
PIT_400_003C_P.PV | P-400-002C Discharge Pressure (PIT-400-003C) | Feed Pressure RO Train - MPD | Process Value in PSI | Applied pressure of the RO feed
PT_200_005C_P.PV | Blower Discharge Pressure (PT-200-005C) | Pressure air discharge Blower MPD | Process Value in PSI
PT_200_006C_P.PV | RO Feed Pump P-200-001C Suction Pressure (PT-200-006C) | Suction Pressure RO Feed Pump MPD | Process Value in PSI
PT_200C_Tags.Q_Filtrate_PV | RO Feed Pump P-200-001C Discharge Flow (Calc.) | Total Filtration Flow | Process Value in GPM | Is this post media filter or cartridge filter?
PT_200C_Tags.Q_RO_Feed_PV | Train C Feed Flow (Calc.) | Flow to RO Unit | Process Value in GPM
PT_400_002C_P.PV | P-400-002C Suction Pressure (PT-400-002C) | Suction Pressure HP Pump MPD | Process Value in PSI
Q_400_001C_P.PV | P-400-002C Flow (Calc.) | HP discharge flow ERS Cir Pump | Process Value in GPM
Q_400_002C | Flow to RO Unit | Feed Flow RO Train | Process Value in GPM
RO_300C_Tags.RO.Recovery | Train C Recovery PV | Recovery RO Train | Process Value in %
CV_900_004_P.CV | Product Off-Spec Valve CMND (XV-900-008) | Product Off-spec valve | Valve Reference
FIT_1000_001_P.PV | Flow Rejected Effluent | Brine Effluent Flow | Process Value in GPM
FIT_900_004_P.PV | UV System Effluent Flow (FIT-900-004)LastSampleDate | Permeate water flow to Post-Treatment | Process Value in GPM
FIT_900_005_P.PV | Dilution Water Flow (FIT-900-005) | Permeate water flow to Lime delution | Process Value in GPM
FIT_900_006_P.PV | Slurry Preparation Water Flow (FIT-900-006)LastSampleDate | Permeate water flow to Lime Batch Tank | Process Value in GPM
PIT_900_002_1_P.PV | P-900-001/1 Suction Pressure (PIT-900-002/1) | Suction pressure Product pump 1 | ppm Process Value in PSI
PIT_900_002_2_P.PV | P-900-001/2 Suction Pressure (PIT-900-002/2) | Suction pressure Product pump 2 | ppm Process Value in PSI
PDIT_700_001_P.PV | CIP Micronic Filter (PDIT-700-001) | Differential Pressure Micron Filters Cleaning | ppm Process Value in PSI
PIT_250_001_P.PV | Not being logged, but no effect on operations/energy | Pressure filter press | ppm Process Value in PSI
Q_Brine_Pumps | Calc Rejected Effluent | Calculated Flow | Calculated Pump flow
PSCA_kW | PSCA_kW | PSCA Measured Power | PSCA power = PSCA_kW * 2.76405
PowerDesal_pf | PowerDesal_pf | CMDP Power Factor
PowerDesal_kVA | PowerDesal_kVA | CMDP Real Power | Desal power = kVA * pf